
Siemens Siprotec As found (AF) and As left (AL) files comparison

1. Save the setting files from the Device.

Graphical user interface, text, application, email

Description automatically generated

1. After finishing tests, disconnect the relay.
2. Reopen DIGSI4 and right-click of AF file to change the file name.




1. Change the name and click okay.

Graphical user interface, application

Description automatically generated

1. Now the name is changed.




1. Double-click the new file name and select Offline.

Graphical user interface, application

Description automatically generated

1. Click Okay and open the window.



1. Go to “Compare parameters….”

Graphical user interface, text, application

Description automatically generated

1. Locate the file required to be compared.

Graphical user interface, text, application, email

Description automatically generated

1. Compare via pressing “Start” and print the results.

Graphical user interface, text, application

Description automatically generated